## Slide 1: *Customer* – Heat Pump + MVR use case Performance and price indication
  Heat Pump Type SHP-STC-S
  Refrigerant: R1233zd(E)
  Estimated CAPEX: xx Mio € * (± 30% accuracy)
  Estimated service cost: ~ xx k€/a** (± 30% accuracy, LTSA)
  Estimated footprint: Heat pump: approx. 30m x 20m
        +Steam compression: approx. 20m x 15m
  Estimated project duration: ~24 months
Solution price & characteristics
Source and sink
steam
tsink, out = 200.0 °C
feed water
tsink, in= 90 ˚C
Pel, in = 6.9 Mwel(gross)
water
tsource, out = 35 ˚C
CASE 1 | xx
Heat Pump
MVR
water
tsource, in = 65 °C
Qsource = 9.0 MWth
REMARK: all numbers and information on this page are preliminary, indicative and non-binding
*standard heat pump installation based on terminal points and scope description on following pages
**standard 10 years LTSA (Long Term Service Agreement), further described on following pages
  Source: water at 65 °C
  Sink: steam at 6.0 bar and 200.0 °C
Psink, out = 6.0 bara
Qsink = 15.0 MWth
msink = 21.6 t/h
msource = 248.4 t/h
System COP: 2.2 (gross)
► 6.0 bar steam